**جدول الكميات لمشروع تأهيل بئر المروج خلف الجدار -جيوس**

**Electro mechanical works for groundwater well no. 15-17/011 in Jayyous.**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item** | **Description** | | **Unit** | **Unit Price /$US** | **Qty.** | **Total**  **/$US** |
| **Electrical and Mechanical Works:**  The contractor shall submit in his offer and supply maintenance manuals, catalogues, characteristic curves, testing certificates, shipping, lading documents and specifications of motors, fittings, mechanical and electrical control devices, cables, wiring and all accessories and ancillaries to complete the work. All to be new and not renewed in accordance with the specified specifications. The contractor should verify the design equipments by conducting field visits to the well and must be before ordering any equipment or materials as follows: the contactor must check and verify and match between the reality and the design quantities mentioned in this tender. If he notices any difference or no matching, then he must inform the supervisor engineer and find together a suitable solution to such conditions. This include checking and fitting all dimensions mentioned in the tender as the well's hole diameter, discharge head inlet and outlet. The quantities mentioned in this contract are the best estimate of information we got for this well. The contractor should be responsible technically and financially to supply the suitable materials and transport it behind the wall and upon his responsibility. The tender prices include all works and connections including the electrical and mechanical fittings. | | | | | | |
| **1** | | **Electric Motor:**  Disjoin the existing motors and fittings, and then move it outside the operation site to the place within the **Al-Mrooj** area specified by the project committee. Supply, transport, deliver, install, and operate successfully according to the specifications in the tender on the reinforced concrete foundation a new vertical hollow shaft Electric Motor with suitable reinforced foundation. The motor has to be inverter duty as 10:1 (6-60 Hertz) Speed Range Constant Torque voltage 220/380-440. The motor shall be of standard construction and suitable high thrust bearing to carry the loads of the rotating radial thrust, equipped with weather protection as IP56 type-1 standard, insulation class F complete digital thermal protection unit, complete current overload unit. The motor must be not less than  **80 horsepower at 1500 rpm**, set at continuous steady state 75% -90% of variable/full load and service factor 110% when necessary. Price include 1 year warranty starting from the date of the handing over certificate or 7000 working hours and whichever comes first; price involves removing existing concrete casting and casting suitable reinforced concrete base for the new motor which fits the motor dimensions and its height matches level to the last vertical shaft discharge head. The concrete used should be B-300 and the two meshes a steel box and bars diameter 10 mm. The price includes all works to disjoin the motor, the discharge head and pumping pipes as necessary. The price includes supplying all cables and materials and executing all electrical connections needed between the following elements and despite of the lengths required: A- a cable one in between the main 3-phase power source at the well site (Diesel Generator) and the Main Electric Control Board inside the pumping room B- a cable between the Main Electric Control Board and the electric motor. The cable size and specifications are as follows: All above cables are to be round, blue or green color, copper conductors are solid and made of pure copper EPR, (see annex cable properties). Conductors size **3x70 + 1x35 mm2**. The price includes all materials and works to install the above cables including whatever of electric, mechanical fittings and accessories as PVC and steel trenches, anchors with clamps, jumpers, stays including base, anchors steel wires, The cables must be lay inside 4"PVC/as rubber pipes of flexible spring type two layers. The price includes excavation inside all types of soil and rock trenches not less than 40\*30 cm and lay the cable inside these trenches and adding pure sand as backfilling to all size of the trenches and casting in the last 10 cm of the trenches with plain concrete over the pipes. The price includes supplying and installing all electric motor control devices (as RTDs thermal, over load) and any other connections including cabling inside or outside the pumping station relevant to this work and according to standard specifications for this work. The opening tender committee will receive an offer about type and motor specifications, catalogues, and an in site testing report which shows that the motor is matching with these specifications.   * The price of this item includes supplying and installing two I steel section (25\*30 cm\*8mm) to hold on the motor and discharge head. * The electrical motor must be supplied **with RTD (PT100)** temperature protection. The type of motor connection must be suitable to present the motor temperature digitally inside the control panel. The price of this item includes all costs of materials and works to install and test the RTD control device. * The motor shall be designed and built for 24hr continuous service at any and all points within the required range of operation without overheating, cavitations, excessive vibration and strain. * Motor has to be new and furnished with a stainless steel name plate with data of the serial number, speed , KW, input voltage, Full load, Hz, power, etc . * All works necessary for transporting, supplying to the site of work, installing, connecting, running and testing are under the contractor expenses. * All works must be according to the Palestinian standards and engineers instructions and the specifications and drawings. * The price also includes any missing works not mentioned to execute this work.   The contractor must submit the motor specifications, certificate of origin , catalogues and on site testing report which shows that the motor is matching with the manufacturer specifications | L.S | 10000 | 1 | 10000 |
| **2** | | **Main Electrical Control Panel Unit**: Price includes disjoin existing control panel, supply and install suitable control panel for pumping **60 m3 @ 180** meter, and installing in the site for the mode of operation, a control board according to the following specifications and supervisor instructions: control panel box shall be made of three compartments and the price for this item include all equipments and works mentioned below: The first compartment is for main hour meter and fusses- Main breaker. The second compartment is for the **100 hp** inverter as ABB, or equivalent as shown specifications A4-1, main breaker as Siemens, contactor, capacitor(s) bank, main cables inlet/outlet.), It shall be IP56 protected, thermally painted paint as (RAL 7302). All main cables and wiring must be closed with special plastic cover and protected against human electric shock. The third compartment includes all control circuits, and secondary contactor, breakers for the high voltage cabinet or the low voltage. The control panel must be sealed from all side and fixed to the wall by ten Jumbo screws and laid on a reinforced concrete foundation 40-50 cm above the ground. The contractor should submit **as built** drawing including soft and hard copy. In case the contractor will use any digital equipment including PLC he must submit the cable, the software, laptop computer and all other accessories that are necessary to operate and maintain these digital plc equipment; meanwhile to train the well’s operator how to use and program the PLC and control panel and all installed equipment in this tender for 9-hours minimum.  The labeled nameplates should be mounted at the front of the main board behind the doors and above every switch and group of lamps. Control electric lamps 24v must be fixed to control all operation system, the starter shall be used to start, run, stop , protect and control manually and automatically by using the general required installation of the following equipments completely. The price for this item includes:   * The power circuit must consist of the following: main circuit breaker MCCB **3\*170A**, 25KA adjustable for the company and for generator (MOLLER) two pieces. * Bus bar 200A/0.4KV (3 phases and neutral and earth) * Complete 4p \* 20KA surge arrestors of replaceable type. With box fuse 3\*63. * Digital screen **inverter 100 hp**, Solid state frequency converter as ABB type (with bypass contactor **120 hp** as MOELLER type) equipped with over /under load, over temperature and all control system needed with all protections rated at suitable power that matches the pump motor with (0.8-1.2) over load range.   **Capacitor Banks**: Standby capacitor banks with discharge resistors compensating reactor dry type 400v 50 Hz to reach power factor **0.97** Ducati. Three phase capacitor with resistors **20 KVAR** as Ducati type.   * **Digital multi meter** which is able to read directly from a screen (V, Hz, KW, A, PF). * **No voltage phase sequence and phase failure relays** of best quality as MOELLER. * **On-off push button** set and emergency off button. * **Reset push buttons** red color 22 mm. * **Overload relay** unit rated at 1-1.5 of motor full load including digital motor screen protection control board. * **Temperature relay unit** rated at the motor thermal sensor, including digital motor screen protection control board with all cables and connections. * HRC fuses 3\*63A complete Fernaz type. * **WHM** 50\*50mm. * **24h clock** with 150 hr mechanical reserve. * **Suitable automatic breaker** with adjustable thermal and magnetic protection (ISC>=25KA) NZM. * (0-500V) 96\*96mm Voltmeter with selector switch between phases and neutral. * 3 phase fuse holders set , 10\*38mm , with 20A fuses , * **Suitable earth leakage relay** class A (AC and Dc trip). * Contactor with discharge 25KVAR Moeller type. * **Breakers** for service Siemens type. * **Relays** and timers 24 V for no flow switch and high-pressure, low-pressure sensors. * **Three phase 50 Hz** 400V (KWh-meter), /5A-200/5 CT’s. The KW-h meter as electromechanical meter or solid state and pre-paid card electric type. * **24V/ 50Hz** indication lamps installed in front of the control cabinet.. * **3 position** selector switch A-O-M. * 220-2\* 12V (AC) transformer 100VA. * the price includes all cables to be used for control purposes shall have the following cross section: * (**3\*70 mm2 + 35 mm2**) for the internal connections inside main board and the contractor has to check and order the exact required length. * \*1.5 mm2 for the driving wheel circuits. * \*2.5 mm2 for the circuits of tension measurements. * \*1.5 mm2 for the sensors. * \*4.0 mm2 for the circuits of intensity measurements. * \*All terminals shall be carefully protected to assure electrical insulation. * Switches, measuring instruments, and warning lights shall be installed in the front side of the panel. * The control panel shall be manufactured with enough space (minimum 40% free space of the total size) to insure easy maintenance and no interface between the wiring for all circuits. * **All wires must be coded** clearly and fixed with special wire heads to avoid loose connection. * **All timers (PSK)**, relays and contactors shall be of best quality as Siemens * The contractor shall supply any other materials and devices that might be missed here and considered to be essential to complete the work without claiming any changes in unit prices. * The control panel must be equipped with an **alarming bell** (100 dB at 8 meters distance) and flashing red alarm (should be visible from 300 meter during day). Alarms for all cases of failure as: voltage drop, no voltage or phase failure high or low pressure and no flow, high temperature etc. * The control panel must be equipped with control circuit for either the probe water sensor or to build digital screen for hydrostatic water level sensor. * Temperature control as digital screen * The alarm must be muted without general reset and there should a special button in the front door to stop it alone. * Circuits must consist of the all necessary materials to operate and protect the system automatically and manually, the wiring color system, numbering all the components. The price includes the design of the whole system of control the contractor is intending to carry. The contractor should also submit at the end of work a s built drawing.   The control panel deign should include:   * Transformer 230/24V 150VA * Water level relay HK type. * 220V AC /80 Watt with **2 fans in each compartment**, one for taking in air and the other for taking out the air with grid ( for the panel) complete with thermostat protection. * SIREN (alarm system)   Alarm system 24V for :   1. High pressure outlet 2. Low pressure outlet 3. No flow (non return valve) 4. Soft start fault 5. High temperature  * The price includes all works, as excavation works for installing pressure switches, flow switch and level sensor and all the electrical parts with suitable conduits and metal ducts to complete the works. * The price includes installing and testing for the mode of operation all mentioned devices and sensors. The control panel must be equipped with earthling unit so the price includes. * **Earthling** : The price of the control panel includes supplying and installing complete earth unit with earth equalizer compressing **C40 box copper B.B. 25** mm2, with minimum two concrete manholes as foundation lines , two earth electrodes, D>19m, L=1.5m and any other missing materials to earth the pumping station . The price includes testing earth unit so as to fulfill the standard requirements (resistance less than 1.5-2 ohm). The across different fittings in the piping system. * The price also include supply all materials (as cables, in-out sockets and install, two outlets as 3-phase complete service unit for the pumping room including Main MCB 5\*20A -10 KA MOLLER type. MCB 2 \*10A – 10KA Moeller type the control * The price include all cable materials and works to conduct the electrical connections of the thermal sensor inside the motor -(the cable 3x2.5 mm2 , the cable should be of suitable length. Use flexible thermal conduits, cable glands, wire terminals& labeling at both ends and all the accessories needed to complete the work(excavation &backfilling),the cable from the MDB to the head of pump motor. * **Wiring and Lighting the pumping room** Supplying and executing all materials needed for inside and outside lighting of the station (pump and station yard) including all works, trenches, cables, sockets etc. according to the following: * Supply and install 2x36 W flourcent surface mounted (water proof) IP56 for outside the room * One phase sockets number three * Lighting the room from inside by three double-glass fluorescent lamps (36 w) in each room (water proof). * 2x30w emergency 10 hours duration lighting fixture to be fixed in accordance with the supervisor engineer's instructions. * The lighting service should be controlled by a separate DGB. Its power source is directly controlled through a double pole MCB. * Lighting the outside of the rooms by External two projectors each of 250W Metal Halide water proof IP 56 with aluminum body (high quality) (the price includes all materials and works to carry the inside and outside wiring and lighting. The projectors, will be switched on from the service DGB. Distribution box for lighting suitable for 24 circuit breaker (DBG). Also the price includes conduits, (3x2.5mm) and all size of cables& all accessories needed to complete the work. Supplying materials and executing 3 intake power sockets, and another one as 3-phase and the other three as 1-phase. The price includes supplying electric cables, leads, on-off keys, power sockets, trenches…etc. The price includes all any other missed works or materials to execute the lightening item. | L.S | 8000 | 1 | 8000 |
| **3** | | **Flow Control switch**: Supplying and installing an electrical flow switch suitable for 6" pipes, powered by a 24v-dc power source. Price includes all cables and protection conduits required to connect it with the control panel, as shown pumping layout view. | Num. | 100 | 1 | 100 |
| **4** | | **Pressure barrel**: Supplying and installing of a pressure barrel. The contractor shall supply and install all the pipes and fittings to connect with outlet main 6” pipes of the pump and should be according to specifications. The price include, complete instrumentation of the pressure barrel including all fittings and steel pipes ½” , and two-1/2 inch ball valves, pressure stabilizer needle valve at the entrance, foot valve-4directions, couples, nibbles, elbows with nuts, bolts, flanges and gaskets as needed to install the pressure barrel. The price includes supplying and installing all necessary materials and works to connect to the pressure switches and casting a suitable reinforced foundation under barrel, and above the pump ground level, as shown pumping layout view. | Lump  sum | 400 | 1 | 400 |
| **5** | | **Pressure Control switch** Supply and install two pressure switches 1-25 bar. Price includes all cables and protection conduits required to connect it with the control panel, as shown pumping layout view. | Num. | 125 | 2 | 250 |
| **6** | | Supply and install pressure 2” **Relief Valve**, 16 atm, complete, The price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve and according to specifications Annex 1/ S7. The Price also includes supplying and installing 2" coupling, 2”conical record, 2”nipple and 2" gate valve, as shown pumping layout view. | piece | 700 | 1 | 700 |
| **7** | | **Gate valve**: Supply and assemble gate valve, 6"complete, 16 bar. Price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve. The valves could be installed anywhere within the project area and according to specifications mentioned in Annex1, S2 , as shown pumping layout view. | Num. | 400 | 1 | 400 |
| **8** | | **Gate valve**: Supply and assemble gate valve, 3"complete, 16 bar. Price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve. The valves could be installed anywhere within the project area and according to specifications mentioned in Annex1, S2 , as shown pumping layout view. | Num. | 300 | 1 | 300 |
| **9** | | **Gate valve**: Supply and assemble gate valve, 2"complete, 16 bar. Price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve. The valves could be installed anywhere within the project area and according to specifications mentioned in Annex1, S2 , as shown pumping layout view. | Num. | 50 | 1 | 50 |
| **10** | | **Non return valve**: Supply and assemble a non return valve, 6" complete, 16 bar of the swing type .Price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve. The valves could be installed anywhere within the project area according to specifications mentioned in Annex 1/ S1, as shown pumping layout view. | Num. | 900 | 1 | 900 |
| **11** | | **Compound air valve**: Supply and assemble 2" compound air valve complete, 16 bar. The price includes excavation, cutting, welding, adding screws, bolts and accessories that are needed to assemble the valve. The valves could be installed according to specifications mentioned in Annex 1, S3. The Price also include supplying and installing 2" coupling, nipple and 2" gate valve. , as shown pumping layout view. | Num. | 400 | 1 | 400 |
| **12** | | **Pressure gauge**: Supply and assemble pressure gauge, 25 bar with oil liquid Rotal ASME, B40. Price includes excavation, cutting, welding, adding coupling, and accessories that are needed to assemble the gauge, as shown pumping layout view. | Num. | 50 | 1 | 50 |
| **13** | | **Dresser:** Supply and assemble 6" dresser complete. Price includes ears 60 cm rods and screws, bolts, excavation, cutting, welding, and adding accessories that are needed to assemble the dresser with NP 16 bar, as shown pumping layout view | Num. | 125 | 1 | 125 |
| **14** | | **Dresser:** Supply and assemble 3" dresser complete. Price includes ears 60 cm rods and screws, bolts, excavation, cutting, welding, and adding accessories that are needed to assemble the dresser with NP 16 bar, as shown pumping layout view. | Num. | 100 | 1 | 100 |
| **15** | | **Dresser conical record:** Supply and assemble 2" dresser complete. Price includes rods and screws, bolts, excavation, cutting, welding, and adding accessories that are needed to assemble the dresser with NP 16 bar, as shown pumping layout view. | Num. | 70 | 1 | 70 |
| **16** | | **Steel pipes**: Supply and install 6" steel pipes for irrigation network. The minimum thickness of pipes is 4 mm as shown in Annex 1 /S9. The price includes, all costs of transportation, pipes distribution, excavation, cutting, shaping, welding, painting two faces (red oxide priming paint and zinc oxide base oil paint). The price includes reconnecting the new installed pipes with old network pipes and adding new connections (2", 3" or 4") of similar sizes for all farms which exist on the old pipe line. | M.L | 30 | 6 | 180 |
| **17** | | **Galvanized 3” pipes**  Supply and install 3” diameter galvanized steel pipes thickness 3.96 mm, and according to specifications Annex 1/ S1-9, as shown pumping layout view. | M.L | 15 | 6 | 90 |
| **18** | | **Galvanized 2” pipes**  Supply and install 2” diameter galvanized steel pipes thickness 3.96 mm, and according to specifications Annex 1/ S1-9, as shown pumping layout view. | M.L | 12 | 6 | 72 |
| **19** | | **Elbows, T or Saddle OR Elbows:** Supply and install 6"/90 or 45 degree black steel elbows or T and Saddle for welding SCH 40 anywhere within the project area | Num. | 40 | 2 | 80 |
| **20** | | Supply and install a complete 6" **cast iron water mete**r according to ISO 4064 (class B) or equivalent annex 1/ S5. Capacity 200 m³/hr, 16 bar painted with epoxy coated from both inside and outside, the measuring unit should be removable type without removing the body Price includes excavation, cutting, welding, adding dresser, flanges, screws, bolts, gaskets and adding accessories that are needed to assemble the valve with the dresser. | Num. | 1000 | 1 | 1000 |
| **21** | | **Water Cooling Tank:** Supply and install plastic polyethylene water tank capacity 1 m3 for cooling and lubrication of the shafts and rubber joints before the start according to PSI 99-1 to 6-1999. The price includes supplying and installing all necessary connections as 1-inch galvanized steel pipes, 1-inch ball valve, 1-inch dresser, 1-inch elbows etc. to connect between the water tank and the opening of the outlet at the discharge head, as shown pumping layout view. | Num. | 400 | 1 | 400 |
| **22** | | **Supply and install diesel generator (DG):**  Supplying transporting delivering and installing, and operating on the concrete foundation a new diesel Generator. Set at **continuous steady state** of variable/full load rating at site in ambient temperature at site in ambient temperature of (**45 Co**) at elevation of -120 m a.m.s.l) and **35%-90% relative humidity** without de rating complete as following :   * Water – cooled, **6 cylinders inline**, 4 cycle direct injection, turbocharged and charge air cooled. * Gross continuous power (output at variable load) = **150 K.V.A.** 10% overload power for 1 hour in 12 hours * phases : **3** * At **power factor** (cos ∅ )= 0.95 * With voltage = **220/400 V.** * Phase with frequency =3 ph-50/60 HZ. * Engine operation speed (n) = **1500 r.p.m**,. 4 cycle water cooled engine * The general specification shall be complete as the specification attached with tender * Production year not less than **2020** * **exhaust silencer** with flexible pipes, and other needed accessories * **shutdown solenoid** * insulation class **H** * Control panel and alternator protection class **IP56**   **Air inlet system** :  Dry cartridge type air filter,  **Circuit Breakers**  **3 Pole molded case** circuit breaker mounted on the generating set in a vibration isolated sheet steel box  **Control Panels**  A Series Control Panel must be set mounted key start panel in vibration water and dust proof IP65 sheet steel enclosure with a hinged lockable door. And microprocessor controller  **The control panel is equipped as follows**:  a) Instruments: Voltmeter, Ammeter, Frequency Meter, Hours run meter, Temperature, Coolant temperature gauge, Oil pressure gauge, Battery Condition Voltmeter, rpm meter, alarm horn  b) Controls: Run/Stop Auto Control switch, Voltmeter Phase selector switch   * Ammeter Phase Selector Switch Emergency Stop Button, Lamp test button, * Electronic voltage regulator with no load to full load deviation -+ 2%.   3 Attempt start timer,  c) Shutdown Protection Devices with Indicators for: **Fail to start protection,** **High Coolant Temperature,** **Low oil pressure**, **Low Voltage**, **Over Speed Shutdown**.  d) DC and AC Wiring looms  **Cooling System**  Tropical water radiator and Cooling fan, to cool the engine in ambient temperatures up to 50 deg C (122 deg F)   * Coolant Drain valve * 50% Anti-freeze (Protection to -36 deg C)   **Fuel System**  Daily Fuel tank as recommended by the manufacturer complete with contents indicator, fuel fill cap with breather, fuel feed and return lines to engine and drain plug, including alarm to indicate the low level of fuel. Fuel hydra-mechanical governor or approved equal.  Full set of operation and maintenance manuals circuit wiring diagram and commissioning/ fault finding instruction leaflets,  **Lube System**   * Full pressure flow lube oil filters * Lube oil drain valve   **Mounting System**  Engine and alternator assembly isolated from the steel base frame using anti-vibration mounts. Fan, fan drive and battery charging alternator drive fully CE guarded for personal protection. Base frame incorporates integral fuel tank with capacity for approx. 8 hours running  **Starting/Charging System**   * 24 Volt system with battery charging alternator guaranteed for 2 years * Axial type starting motor * High capacity maintenance free lead acid starting battery * Battery rack mounted on the generating set base frame . Heavy duty interconnecting cables with terminations   **General**  All equipment must be guaranteed for a period of (5,000 working hours or two years which ever finishes earlier) from the date of commissioning  **Alternator System**   * Screen protected and drip-proof * Self exciting, self regulating brushless alternator with fully interconnected damper windings   **Tests**  Generating set is load tested and all protective devices and control functions are simulated and checked before dispatch  **The prices shall includes :**   * Installing and fixing the D.G. set on the concrete foundation inside the proposed room. * Executing all 1/2” fuel connections pipes as needed and operating the unit as required. * The D.G. set must supplies with new battery (2x24v-160/180A.H.) or as needed with high efficiency and quality, with suitable cables * Other standard parts and instruments needed for good operation. * The concrete foundation box with two steel meshes of each of 8 mm steel bars at 15 cm in all directions. The length and width and depth should match the D.G dimensions. * Executing and fixing the exhaust silencer, flexible pipes needed 4" and the necessary piping to connect it complete as required. Executing all 1/2” fuel connections pipes as needed and operating the unit as required price includes changing oil, oil filters, fuel filters, and any other parts necessary to change within the first 100 operating hours, and the including the diesel required to run the first 10 hours only. The opening tender committee will receive an offer about type and motor specifications, catalogues, and an in site testing report which shows the motor is matching with these specifications. | L.S | 25000 | 1 | 25000 |
| **23** | | **Old Pump lifting and installation new pump.** All works related to lifting old turbine and installation of new turbine including preparing the site, remove and reinstall the discharge head, pumping pipes, turbine, shafts, rubber joints, access pipes, retainers and all related accessories. The price involves checking and operating the pump after finishing all project works to insure no vibration or unusual sound. The price includes all machines and labor works related to well's pump installation. | Lump sum | 2000 | 1 | 2000 |
| **24** | | **Vertical Turbine Pump;** Supply and install a multi stage vertical pumping turbine complete (pump, screen, shaft bowels, stages, connection head to the **5 inch riser pipes**, and all related accessories) all as specified in the technical specifications attached with the tender. The price includes any other works to achieve the required head and quantity and efficiency. The main pumping data as follows:  Current well total well depth is **125** meters; and the well hole is **10”** and must be checked and verified. The intended pumping pipes diameter is **5”**; and the total pumping pipes length inside the well is **115** meters(all given information on existing well data and figures must be checked and verified before order any quantities), and dynamic drawdown is not known. Static water level is around **95-100** meters below surface. The turbine properties is fit as follows:   * Liquid water is potable for human drinking and suitable for field60 **60 m3/hr** * Design anticipated total head at the intended turbine discharge **180** m. * Maximum pump column and discharge head assembly head losses (m): 3 * Shut-off head limits (m) min not less than **235 m**. * Turbine overall efficiency at the working point is not less than 73%. * Min bowel efficiency at run out capacity 80%. * NPSHA at max run out capacity (m) :8 * NPSHA at max anticipated TDH (m): 5. * Pump operating speed (rpm) :**1500** * Maximum pump diameter (inch) :8” diameter: * Closed impellers manufactured from bronze and cast iron bowels. * Stainless steel column, stainless steel screen filter * The well pump shall be capable to run at shutoff head for a few minutes without mechanical problems. * The turbine torque design should be duty inverter at speed range the design values between 1:10 * The price includes supplying and installing all required flanges, coupling, reducers, bolts, spacers, sleeves, nuts, etc. to connect between the turbine outlet, turbine column and the rising pipes and shafts accordingly. The price also includes casting concrete foundation and I steel sections to should the turbine. The price includes all repair works as a result of old turbine disjoin or new turbine installation. * The contractor shall do in site testing the turbine in accordance with well hole, static water level, dynamic water level, well over all depth, and submitting the test report. Before ordering or installing any new materials, the contractor must get the initial records for existing conditions of the well including: the well pumping capacity in m3/hr, water level inside the (dynamic and static). Therefore, the contractor must prepare suitable water meter and water level meter to carry on these measures. Therefore, the price of the turbine includes the costs of all these tests. In case the contractor failed to get these measurements, the turbine price will be less by 30% than the price proposed in his tender. | Lump sum | 17000 | 1 | 17000 |
| **25** | | **Pumping pipes**: Supply and install new seamless iron pumping pipes with the following specifications should be supplied: **(SCH 40)** Diameter 5”, thickness not less than 7.1 mm; and teeth not less than 8 teeth in 1" and painted with epoxy from outside and inside. The number of teeth should be enough to cover the whole length of the intended coupling joint is not less than 13 cm length. The price includes threading cutting and adding reducers, or flanges, bolts to connect between the new rising pipes and the pump and the discharge head. Taking in consideration that the quantity estimated in this tender may increase or decrease. | M.L | 110 | 15 | 1650 |
| **26** | | **Shafts:** Supply and install new shafts of carbon steel 1040, of 35 mm diameter and at the joints should be covered by stainless steel sleeves, and ended with a threaded stainless steel couple. The price includes threading, cutting, adding suitable line shaft coupling, stabilizers to connect between the new shafts and the pump. Taking in consideration that the quantity estimated in this tender may increase or decrease. | M.L | 60 | 15 | 900 |
| **27** | | **Retainers and bearings:** supply and install new bearing retainers made of bronze and taking in consideration that the quantity in this tender is estimated and may increase or decrease. | Num. | 90 | 5 | 450 |
| **28** | | **Rubber Joints**: supply and install new rubber joints and taking in consideration that the quantity in this tender is estimated and may increase or decrease. | Num. | 10 | 5 | 50 |
| **Total costs of all materials and works** | | |  | | | **70717** |

**Costs Summary**

|  |  |
| --- | --- |
| **Item Cost** | **Total amount /$US** |
| **All Mechanical and Electrical works for the groundwater well. 15-17/011** |  |
| **Total in words (includes) –$US** | |

**Company / Contractor Name: --------------------------------------------**

**Address: -----------------------------------------------------------------**

**Telephone: -------------------------------------- Fax: ---------------------**

**Signature and Stamp: --------------------------------**

**Date: -----------------------------**

**General Information well 15-17/011**

**Data collected** according to well operator experience.

Location: Jayyous-Qalqilya, Al-Mrooj Area

Coordinantes: X= 150275 Y= 180209, Z= 115 a.m.s.l

ID Number: 15-17/011

Year of Establishing: 1965

Method of Drilling: Tool Percussion

Total Depth: 125 meters

Static Water Level: 100 meters below surface

Pump Setting: 115 below surface

Diameter of Drilling: 10”

Existing Pumping pipes diameter: 5”

Existing Pumping Capacity: 60 m3/hr

Irrigated Area: 300 Dunums

Number of farmers: 60

Average working hours in summer: 300 per month

Average working hours in winter: 100 per month

**Annex 1: Fittings Materials Specifications**

**A-S1: Check valves**

1. Body: Cast Iron
2. Disc: Cast Iron
3. Cover: Cast Iron
4. Seat Holder Cast: Iron
5. Body Seat Ring: Bronze ASTM B62
6. Disc Seat Ring: Rubber (BUNA-N) ASTM D 2000 AA 7008
7. Hinge Pin: Stainless Steel
8. Plug: Malleable Iron
9. Cover: Bolt & Nut: Steel
10. Seat Holder Bolt: Stainless Steel
11. Cover Gasket: Rubber (BUNA-N)
12. Coating: fusion bonded epoxy inside and outside

**A-S2: Gate valves none rising stem:**

1. Body: Cast Iron
2. Bonnet: Cast Iron
3. Packing Box: Cast Iron
4. Disc Cast: Iron
5. Hand Wheel: Cast Iron
6. Body Seat Ring: Bronze
7. Disc Seat Ring: Bronze
8. Gland Cast: Iron
9. Stem Nut: Bronze
10. Stem Bronze
11. Bonnet Gasket: steel
12. Packing Box Gasket: steel
13. Bonnet Bolt & Nut: Steel
14. Gland Stud & Nut: Steel
15. Packing Box Stud & Nut: Steel
16. Top Nut: Steel
17. Washer: Steel
18. Packing: Graphite Fiber Commercial
19. Operating Nut: Cast Iron A 126 Class B
20. Coating: Electro statically applied epoxy inside and outside,

**A-S3: Combination Air Valve**

1. Body: PN21 Sphere Nodular ASTM-536 60-40-18
2. Rolling Seal: Rubber E.P.D.M
3. Clamping Stem: Reinforced Nylon
4. Float: Foamed Polypropylene
5. Base: Brass ASTM B-124
6. O-Ring: Buna-N
7. Cover : PN21 Cast iron ASTM A-48 CL-35B
8. Nozzle Seat: Bronze ASTM B-62 B-271 C83600
9. Nozzle Seal: Rubber E.P.D.M
10. O-Ring: Buna-N
11. Bolt and Nut: Galvanized Steel, Chromate Plated
12. Float: Stainless Steel 304L
13. Body: PN21 Cast iron ASTM A-48 CL-35B
14. Sleeve: Reinforced Nylon
15. Threaded Outlet: Brass
16. 16: Coating: fusion bonded epoxy inside and outside

**A-S4: Butterfly Valves: (GEAR)**

1. Stem: Stainless steel
2. Body: Cast iron
3. Bushing: Brass
4. O ring: EPDM
5. Bushing (spacer): Polymeric
6. Disc: Stainless steel
7. Liner: EPDM
8. Washer: Bronze
9. Retaining ring: Spring steel
10. Plug: Plastic
11. Coating: Fusion bonded epoxy inside and outside

**A-S5: Water meter specification and materials.**

1. Working pressure 16 or 25 bars as required.
2. Max. temperature 60 C
3. Body: cast iron
4. Coating: epoxy
5. Connection: Flanged ends

**A-S6:** **Strainers Specifications:**

1. Body: cast iron ASTM 126 class B
2. Cover: cast iron ASTM 126 class B
3. Screen: stainless steel
4. Gasket: Buna -N
5. Plug: steel
6. Bolts: steel
7. Coating: fusion bonded epoxy inside and outside

**A-S7: Control Valves specifications (float valves and pressure reducing valves)**

1. Connection: flanged
2. Water temperature up to 60 C
3. Working pressure 25 bars
4. Valve body and cover ductile iron (ASTM A-536)
5. Valve internals: stainless steel and bronze
6. Control trim: brass
7. Elastomers: Buna-N
8. Coating: fusion bonded epoxy

**A S-8: Painting works include** adding two faces (red oxide as priming paint and zinc oxide base oil paint for finish). The pipe surface must be painted with two coats from all sides, particularly lower part to the ground. Therefore, the pipe must hold on supports above the ground minimum 30 cms, and then released to ground down after the paint was dry. Prepare the surface and stir the paint before use or mix using a power agitator. Before applying paint, a thinner liquid has to be added to the pipes surface to clean away oil and grease, use a detergent to remove excess dirt and contaminants. Remove the metallic debris such as mill scale and rust using disc sanders, sandpaper or wire brushes which ensures an adhesive surface.

**A-S-9: Carbon steel line shafts: According to ASTM A576**

**A-S-10: Irrigation Steel Pipes Welded Black Steel Pipes,** [**ASTM A53**](http://www.techstreet.com/cgi-bin/detail?product_id=911886) **or as API5L:**

**A53 Type F**, which is longitudinally furnace butt welded or continuous welded (Grade A only),

**A53 Type E**, which is longitudinally [electric resistance welded](http://en.wikipedia.org/wiki/Seam_welding) (Grades A)

**B- The Vertical Hollow Shaft Electric Motor Set** shall be complete with the accessories and ancillaries needed in accordance with the following specifications:

* An efficient approved engine speed 1500/1800 rpm inverter duty VFD and fitted to maintain engine speed at all condition of load.
* The cooling system shall be a closed type with, class F insulation, temperature rise class B, and internally built thermal senor to be connected to the MCB.
* The Electric Engine set shall be mounted on a suitable reinforced concrete foundation with common steel frame and no vibration and high thrust capacity
* Other standard parts and instruments needed for good operation. As power factor at full load not less than 90% and efficiency at full load not less than 94%
* Winding design as standard 3-phase motor 415 V, 50 Hz and permissible and preferences for variable speed motor or duty frequency motor (in the range between 10-70 Hertz), tolerance of 10% in voltage in the range 380-480 volt.
* Rated and output power apply for standard ambient conditions of 40-50 C°
* Motor frame, end shields, terminal box are made of cast iron, fan made of sheet stainless steel.
* High capacity bearing, single output shaft of stainless steel
* Degree of protection as standard IP 56
* The offer must be supplied with catalogue (M&O) for the motor set, curves power, efficiency, engine specification and test certificate, etc…
* The contractor is responsible to issue a 1 year warranty starting from the date of the taking over certificate.

**C- Solid state frequency inverter**

* Wide Voltage Range: 320 ~ 480V
* Input Frequency Range: 40 ~ 65Hz
* Output Voltage Range: 0 ~ rated input voltage
* Output Frequency Range: 0 ~ 500Hz
* Overload Capacity: 60s with 150% of rated current, 2s with 180% of rated current
* From 0.75 ~ 7.5KW Plastic house; 11 ~ 630KW is metal house
* Control Mode: High Quality V/F Control
* Speed Accuracy: V/F + 0.5% of maximum speed
* 20 channels for frequency setting
* Analog signal: 0 ~ 10V,-10V ~ 10V,0 ~ 20mA.
* Pulse setting input: 0~50 KHz.
* Built-in RS485 communication port
* Solid state programmable screen and PLC configurations
* All model are integrated IGBT
* The malfunction ratio is 0.8% within 24 months warranty

**D- Cable Specifications:**

The cable is flat with a light blue outer sheath -, drinkable conductors for permanent submersion in potable water, to respective depths and up –to 600 meters. It is water resistance tested to the European standard EN 505825-2-21 (AD8 condition complete submersion in water) and meets the requirements of BS 6920, and IEC 60228 covering the suitability of non-metallic materials and products for use in contact with water. The EPR (Ethylene Propylene Rubber) insulation and Elastomeric Cross-linked outer sheath should provide a robust and water-tight barrier.

The voltage rating is 0.6/1kV and a temperature rating of -25oC to +90oC. It is suitable for use in water of a maximum temperature of 80oC

the conductor main construction properties are as follows:

* Class 5 (Flexible Conductor) fine stranded tinned pure Copper
* Voltage rating: (0.6/1kv) 600 V between the conductor and earth, and 1000 V rms between adjacent conductors.
* Inner Insulation: EPR (Ethylene Propylene Rubber)
* Outer sheath/ Jacket: Elastomeric Cross-linked compound including filler materials
* Conductors sizes as specified in the BoQ, 3GI3 quality insulation). The junction box (Water Proof) and main connection. The cable is fixed inside PVC pipes under the ground and protected by a concrete cover not less than 10 cm. The price includes the costs to carry the cable insulation resistance with megger and connect to control panel.