## mech
BILL No.01
Item | Description | Unit | Qty | Unit Price US $ | Total Price US $
1 | THE COSTS PROVIDED BY THE CONTRACTOR IN THIS BILL OF QUANTITIES ARE ALL INCLUSIVE FOR THE WORK DESCRIBED IN THE DRAWINGS AND SPECIFICATIONS, WHETHER SPECIFICALLY MENTIONED IN THE BELOW DESCRIPTIONS OR NOT.
MECHANICAL WORKS
General
A | Unit prices of all items shall include for cleaning the site from all surplus, backfill materials, or results of excavation, and repairing all damages of concrete, or stone walls, or asphalted yards, edge of asphalted roads, sidewalks, existing water pipelines, sewerage lines, cables, cesspools, etc..., that may occur in the course of executing the works. All according to drawings, specifications, conditions and the instructions of Engineer or his representative.
B | Unit prices also include testing, balancing, adjusting, flushing, disinfections and commissioning of water facility components and handling to the Recipient of complete operational systems.
C | The price of pipes shall include all types of fittings, lowering, mounting, jointing, welding, supporting, trenching works including excavation, bedding, embedment, backfilling and reinstatement.
D | The unit price of all isolating, safety, control valves includes flanges, bolts, nuts, gaskets, spindles, chambers, boxes, supports, fittings, couplers, all necessary accessories, earth works (excavation, bedding, backfilling and reinstatement).
E | The Bills of Quantities, Specifications, Drawings and all other Contract documents are complementary to each other.
F | It is the responsibility of the Contractor to check the locations and quantities of the materials and equipment to be executed in accordance with the contract drawings.
G | The unit rate of the materials and equipment shall be based on the Specification, all components as required and specified under each item concerned in the Specifications, Contract Drawings, and all other Contract documents.
H | In addition to the above mentioned requirements, the Unit Rate shall include the following which are complementary to the mentioned items in the bill of quantities.
h1 | Supply of materials and equipment.
h2 | Off loading and handling from trucks on site to place of installation.
h3 | Installation of materials and equipment.
h4 | All civil works required and connected with the mechanical installations, such as: equipment concrete bases and supports, hangers, brackets, cutting through walls and slabs for passage of pipes and conduits and ducts, pipe sleeves, re-patching, erecting, lowering, mounting of pipes and supports to structure, excavation and backfilling, riggings, hoisting, water proofing, cleaning, protection and painting.
Total
h5 | All labor, materials, tools, instruments needed for perfect operation.
h6 | System identifications, tags, labels, nameplates, and charts.
h7 | Shop-drawings, as built and record drawings.
h8 | Recommended Spare parts, O&M manuals, training and components for ideal running of all services and equipment.
h9 | Samples as required by the Engineer.
h10 | Inspection, testing, rejection, adjusting, balancing, commissioning, and handling to Owner of all materials, equipment and workmanship.
h11 | Maintenance of all items supplied by contractor as per Contract Conditions.
h12 | Assist in testing and commissioning of all mechanical devices which are supplied by others for all equipment and systems as shown on drawings and called for in the specifications.
I | The quantities shown in this bill are estimates and are liable for variation according to actual execution on ground or Engineer orders without any adjustment to contract unit prices.
J | The contractor is not entitled to claim for changing of unit prices in the event of changing pipe routes or equipment locations as a result of technical reasons on ground during execution.
K | The diameters of needed pipes and valves are the nominal diameters. The outside and inside diameters of pipes shall be according to the Palestinian Standards No's 186, 141 or equally approved.
L | Pipes, fittings, valves, accessories, controllers, instrumentation, specials, protective coatings, jointing materials etc. should be according to the latest editions' of standards and references specified in the tender documents.
M | Pipes, fittings, valves, accessories, controllers, instrumentation, specials, protective coatings, jointing materials etc that may come in contact with portable water should not constitute any toxic hazards, should not support any microbial growth, or cause taste/odor, cloudiness or discoloration of water and must be approved by a recognized certifying authorities as being suitable for drinking water.
Total
1 | Well pump
1.1 | Well Turbine Pump: Supply and installations for the perfect operation of Jayous well. | LS | 1
Supply, deliver, furnish, position, install, test, operate, commissioning, disinfect and maintain Deep Well Submersible Turbine pump water lubricated of 120 m3/hr flow against 290 m total dynamic head , shut off head not less than 380m and efficiency not less than 78% complete with all pump parts and components according to specificationscomplete with all pump parts and components according to specifications and drawings (bowls, shroud if needed , pump column rising pipes Column pipes: Supply and installation of steel pipes; 6 inch x260 linear meter , SCH40, epoxy coated from inside and outside surfaces, threaded 8TPI tappered threads, with min. 15cm steel coupling length, each pipe shall be around 6 meters length. Steel pipes shall be according to specifications for submersible pumps use couplings Price including discharge head, mounting plate, 316 SS non return valve with spring and submersible motor , motor capacity as manufacturer recommendation. , with 2960 r.p.m., 3ph - 380 / 415 volt - 50 Hz), motor efficiency not less than 88%.
Note :- Submersible pump motor and pump shall be equipped all requirements to operate the pump with V.F.D /or soft starter systems , the Electrical Motor must be heavy duty with suitable power needed
This shall include all well pump equipment, appurtenances, instrumentation. This item includes the pump foundation, well sounder and well transducer with two lines of access pipes 1.5" PVC-Sch80 or HDPE; one for well level sensor of 260 l.m. (90 l.m. slotted), and the other also 260 l.m. for M-scope measurment, extension of well casing, electrical cable tinned copper, EPR insulation, flexible copper conductor, EPR shealth, operation temperature up to 70C, blue or black according to supervisor engineer instructions. Submersible cable shall be according to PWA specifications for submersible pumps use and for drinking water use.accessories and works for the perfect operations of the well as shown on drawings and tender documents.
1.2 | Supply and install above and under ground 3/16" steel pipe dia 6" and 4" with all fittings from well pump to existing pipeline and from well pump washout to washout including flap valve , price to include flanges elbows 45 and 90, flanges tees, flanges reducer tees , reducers ,adjustable pipe jack support ,hydrostatic pressure leakage test, etc and all necessary fittings to complete the job according to the Specifications, drawings and as direction of the Engineer. ( Price include also the excavation and backfilling for the under ground pipes | LS | 1
1.3 | Supply and install 6" gate valve the price to include flanges,and all accosserios etc and all necessary fittings to complete the job . according to the Specifications, drawings and as direction of the Engineer. | ea | 3
1.4 | Ditto item 1.3 but 4" gate valve | ea | 2
Total
1.5 | Supply and install 6" dismantling Joint , the price to include flanges,and all accosserios etc and all necessary fittings to complete the job . according to the Specifications, drawings and as direction of the Engineer. | ea | 5
1.6 | Ditto item 1.5 but 4" dismantling Joint , | ea | 1
1.7 | Supply and install 2"Air release valve with 2" flange gate valve the price to include flanges,and all accosserios etc and all necessary fittings to complete the job . according to the Specifications, drawings and as direction of the Engineer. | ea | 1
1.8 | Supply and install 6" check valve the price to include flanges,and all accosserios etc and all necessary fittings to complete the job . according to the Specifications, drawings and as direction of the Engineer. | ea | 1
1.9 | Supply and install cast iron pressure relief valves PN16, DN100 mm (4") including all flanges gaskets, bolts and nuts with all related accessories. All in accordance to PWA specifications and engineer approval. Price to include and any other required accessories. | ea | 1
1..10 | Supply and install and welding 1/2'' Coupling with 1/2" Stop Valve( for chlorine injection and well water test | ea | 1
| Supply and install and welding 3/4'' Coupling with 3/4" Stop Valve( for potable water | ea | 1
2 | Chlorination system
2.1 | Supply and installation of chlorination system including two dosing pumps with 2.2 l/hr @ 10 bar, two injector, two multifunction valve, two foot valve, two HDPE 750 lt tank, 50 meters of tubing (special tubing for HCL) with 2" pvc sleeves for tube fan 12" , fittings and any other required to complete and operate the system and also the price include tanks concrete foundation | ea | 1
2.2 | Supply and install above and under ground pipes inside chlorination room and potable water pipes from well pump line to connect the with water tank on the roof and from roof to eyes wash and shower price to include flanges elbows 45 and 90, flanges tees, flanges reducer tees , reducers ,support ,hydrostatic pressure leakage test, etc and all necessary fittings to complete the job according to the Specifications, drawings and as direction of the Engineer. ( Price include also the excavation and backfilling for the under ground pipes | LS | 1
2.3 | Supply and Install PVC Water Tank 500 liter . Price to include 30cm height steel stand base black painted, 3/4" automatic float valves, valves, fittings, vents, and all necessary works to complete works as per drawings. | LS | 1
2.4 | Supply, installation, testing, and commissioning End Suction cold water pump 0.5m3/hr@15m Head . Price including all valves, strainer, pressure control , valves pressure gages complete with concrete base vibration absorber. All are according to drawings, | LS | 1
Total
3 | Electrical room Air coinditioning system
| Supply and install 2 ton ref air coinditioning cooling cap. High wall the price to include copper pipes with insulation , tap , drain pipe , cables between indoor and outdoor units , remote control and any other required to complete , All are according to drawings and as direction of the Engineer. | LS | 1
Total
Total Carried to Summary
Unit Legend:
| lm | linear meter
| sq m | square meter
| cu m | cubic meter
| ls | lump sum
| ea | each

## elec
BILL No.02
Item | Description | Unit | Qty | Unit Price US $ | Total Price US $
1 | THE COSTS PROVIDED BY THE CONTRACTOR IN THIS BILL OF QUANTITIES ARE ALL INCLUSIVE FOR THE WORK DESCRIBED IN THE DRAWINGS AND SPECIFICATIONS, WHETHER SPECIFICALLY MENTIONED IN THE BELOW DESCRIPTIONS OR NOT.
ELECTRICAL WORKS
General
A | Unit prices of all items shall include for cleaning the site from all surplus, backfill materials, or results of excavation, and repairing all damages of concrete, or stone walls, or asphalted yards, edge of asphalted roads, sidewalks, existing water pipelines, sewerage lines, cables, cesspools, etc..., that may occur in the course of executing the works. All according to drawings, specifications, conditions and the instructions of Engineer or his representative.
B | Unit prices also include testing, adjusting, settings and commissioning of all electrical components and handling to the Recipient of complete operational systems.
C | The price shall include all types of Cable Ladder,UPVC pipes for power, control & communication lines , electrical manhole,25TN cast iron cover labeled Electrical, Cables and Wires, supporting, trenching works including excavation, bedding, embedment, backfilling and reinstatement.
E | The Bills of Quantities, Specifications, Drawings and all other Contract documents are complementary to each other.
F | It is the responsibility of the Contractor to check the locations and quantities of the materials and equipment to be executed in accordance with the contract drawings.
G | The unit rate of the materials and equipment shall be based on the Specification, all components as required and specified under each item concerned in the Specifications, Contract Drawings, and all other Contract documents.
H | In addition to the above mentioned requirements, the Unit Rate shall include the following which are complementary to the mentioned items in the bill of quantities.
h1 | Supply of materials and equipment.
h2 | Off loading and handling from trucks on site to place of installation.
h3 | Installation of materials and equipment.
h4 | All civil works required and connected with the electrical installations, such as: equipment concrete bases and supports, hangers, brackets, cutting through walls and slabs for passage of conduits and ducts, pipe sleeves, excavation and backfilling, riggings, hoisting, water proofing, cleaning, protection and painting.
Total
h5 | All labor, materials, tools, instruments needed for perfect operation.
h6 | System identifications, tags, labels, nameplates, and charts.
h7 | Shop-drawings, as built and record drawings.
h8 | Recommended Spare parts, O&M manuals, training and components for ideal running of all services and equipment.
h9 | Samples as required by the Engineer.
h10 | Inspection, testing, rejection, adjusting, balancing, commissioning, and handling to Owner of all materials, equipment and workmanship.
h11 | Maintenance of all items supplied by contractor as per Contract Conditions.
h12 | Assist in testing and commissioning of all electrical devices which are supplied by others for all equipment and systems as shown on drawings and called for in the specifications.
I | The quantities shown in this bill are estimates and are liable for variation according to actual execution on ground or Engineer orders without any adjustment to contract unit prices.
J | The contractor is not entitled to claim for changing of unit prices in the event of changing pipe routes or equipment locations as a result of technical reasons on ground during execution.
K | The cable and wire sizes shall be according to the Palestinian Standards or equally approved.
3 | Well pump
3.1 | Well Submersible Pump : Supply, installations, testing and commissioning for the perfect operation of the well pump. The price include Flat submersible pump cable, with suitable heat shrinkable joint between the Motor cable and the Flat cable Annealed bare stranded copper conductors PVC insulated form a -45 to 75°C 600/1000 Volt Multi-Conductor. The size & length of the cable must be as recommended by the pump supplier, the voltage drop must not exeded 3% of nominal motor voltage. Furnish, install and termination of well pump power cables and control wire, conduits, cables, connection boxes and miscellaneous. The Flat power cable length from the Pump's motor to Junction Box on the well head. and from the Junction Box to the electrical room the contractor to use XLPE Cu cable with the same size of the flat cable. | Ls | 1
3.2 | Furnish, install termination and operation of Submersible Level Sensor (Pressure Sensor), 17.5 mm stainless steel sensor - Measure Range : Ranges from 3.5 to 600 mH2O (5 to 900 psi). - Accuracy: • Accuracy ±0.25% . - Power Supply : 10 - 30 Vdc, Signal Output : 4~20mA. - All welded 316L stainless steel construction. - Vented polyurethane cable with Kevlar® anti-stretch construction. - Level Sensor Accessories: Sensor Termination Enclosure, Cable Clamp. The length of the cable must be from pump seting to the Electrical room. The price include connecting, monitoring and protect the pump from Dry Run | ea | 1
Total
3.3 | Furnish, install termination and operation of Motor tempreture controler, the price include Tempreture controler : controller accepts signals from a variety of temperature sensors RTD (PT100). The controller can also be configured for process inputs including 0 to 5/10 VDC, 0/4 to 20 mA DC, or 0 to 50 mV DC. The PXU can provide an accurate output control signal (time proportional or DC Analog Output) to maintain a process at a determined setpoint value. Dual 4-digit display readings allow viewing of the temperature/process and setpoint value simultaneously.The price including the recomanded cable from motor winding RTD to the Controller in the control panel • PID AND PROFILE CONTROL • ACCEPTS 0-10 V, 0/4-20 mA or 0-50 mV SIGNALS • FUNCTIONS AS A DIGITAL POT (MODEL DEPENDENT) • ON DEMAND AUTO-TUNING OF PID SETTINGS • 2 USER PROGRAMMABLE FUNCTION BUTTONS • PC (MODELS WITH RS 485) OR FRONT PANEL PROGRAMMING • CONTROLLERS MEET IP65 REQUIREMENTS • DUAL ALARMS • DUAL OUTPUTS | ea | 1
3.4 | Furnish, install and operation of well pump ,16 bar Mechanical Flow meter , price to include flanges, and all accessories etc. and all necessary fittings to complete the job . according to the PWA Specifications, drawings and as direction of the Engineer. | ea | 1
3.5 | Furnish, install, calibration and termination for well pump PADDLE TYPE FLOW SWITCH , 16 bar including control wire, conduits, connection boxes and miscellaneous. Suitable for 4" pipe with all mechanical needed. - Housing Material: Aluminum Alloy, IP65. - Operation Temp.: -30 C~150 C. - Paddle Material: SUS304 - Operation Pressure: Max. 355 PSIG. - Set Point Tolerance: 25%. - Contact Capacity : 60W 220V/200Vdc SPD | ea | 1
3.6 | Supplying , installing and calibration a pressure gauge 16 bar, reading scale (0-10) bar complete. With thee way valve | ea | 1
3.7 | Supplying , installing and calibration a Low Pressure switch Regulation range (-0.8 – 5) bar, Different tial ∆p (0.5 – 1.6)bar, Auto Reset, Maximum working pressure 22 bar, including control wire, conduits, connection boxes and miscellaneous. Suitable for 4" pipe with all mechanical needed. IP66 to EN 60529 / IEC 529, except for versions with ext. reset which are IP54, Suitable for alternating and direct current (AC and DC), Interchangeable contact system, Safety Integrity Level: SIL 2 according to IEC 61508 | ea | 1
Total
3.8 | Supplying , installing and calibration a High Pressure switch Regulation range (2 – 18) bar, Different tial ∆p (1.2 – 4)bar, Auto Reset, Maximum working pressure 22 bar, including control wire, conduits, connection boxes and miscellaneous. Suitable for 4" pipe with all mechanical needed. IP66 to EN 60529 / IEC 529, except for versions with ext. reset which are IP54, Suitable for alternating and direct current (AC and DC), Interchangeable contact system, Safety Integrity Level: SIL 2 according to IEC 61508 | ea | 1
3.9 | Supplying, installing and testing Earthing System includes galvanized steel strip 30x3 mm, welded each meter to its base steel structure, 3 sets of 19mm,Dia, 1.5m L,CU rods including 16mm CU wire, pits with heavy duty cast iron covers, 6mm2 insulated earthing of all metal parts that includes cable trays, water pipes, cable ladder, ac units, distribution boards bodies,PEC 40x4x0.4 mm2 in metal box, Earthing and grounding resistance must be =<2 ohm | Ls | 1
4 | Chlorination system
4.1 | Supply, install testing and commissioning of Chlorination control points, for the dosing pumps. controlled from the main control panel to operate and control the dosing pumps, after well pump operate and according to the level of chlorine in the tanks, the dosing pumps well operate alternatively this include all cables, wires, conduits realis, timers, controllers, switches, indicators | ea | 2
4.2 | Furnish, install and termination of FLOAT LEVEL SWITCH for very aggressive liquid mixtures such as sulfuric acid, suitable for chlorination system. Allowed fluid density 0.75 to 1.50,Maximum pressure 2 bars, Maximum temperature 125°C, Protection index IP 68, Electric characteristics 230 VAC - 50/60 Hz, Housing material PVDF, Cable Conductors PTFE,The cable length must be suitable to connect to the control panel without any splices | ea | 2
5 | MDB,Well pump, Electrical, guard & chlorination room.
5.1 | Supply, installation, operate, testing and commissioning of classic control panel, Timers, relays, transformer 230/24V 50VA, digital multimeter, selector switches, pushbuttons, alarm system including ps, buzzer, LED indication lights, VFD for well pump (1.2X pump electrical motor size) , electric protections, cabling with related equipment and general electric cabinet, trenches and all the necessary accessories. The price include power and control cables from the control panel to well junction box. Power and control cables from the control panel to chlorination dosing pumps. The pump must operate Automatically using 24h timer or Manually in the two options the pump well stop if High pressure, low pressure, flow switch, Motor High Tempreture or VFD fault occur. The VFD must be caliprated and protect the Motor from Phase Failure, Torque, Voltage spike, Over Current | ea | 1
Total
5.2 | Supply, Install and Connect Main Distribution Board according to IEC 61439 & GTS . Price to include metal panelboard oven painted 2mm thickness Waterproof, all cables required to connect well pump, guard Room, Electrical room, chlorination room and external light, according to design drawing. space for future ATS, Molded case Main circuit breakers MCCB with minimum breaking capacity of 25 K.A thermal and magnetic protection, miniature circuit breaker MCB with minimum breaking capacity of 10 K.A., bus bars, volts & amps- Measuring instruments, voltage arrestor and space for KWHM, phase failure, Surge arrester according to electrical utility requirements. Also to include main earth bus bar as drawings and specifications with all necessary circle works. The type of MCCBs, MCBs, VFD and main components are Siemens, ABB, Eaton, Schneider or equivalent - Main Power cable from the utility to MDB 2X(3x150+70). | ea | 1
5.3 | Supply, Install and Connect,Main Power cable from the utility to MDB 2X(3x150+70).XLPE, Cu, 1KV, according to electrical utility requirements & instruction | lm | 50
5.4 | Supply, Install and Connect, Power Cable from VFD to well Junction Box (3X185+95)XLPE, Cu, 1KV | lm | 25
5.5 | Supply, Install and Connect 16A 3-pin power socket, conduit, wires | ea | 4
5.6 | Supply, Install and Connect 16A 3-pin power socket water proof,conduit, wires | ea. | 3
5.7 | Supply, Install and Connect 20A, AC socket for split units, conduit, wires | ea. | 2
5.8 | 16A 5-pin power socket water proof | ea. | 1
5.9 | Supply, Install and Connect Hot Water Cylinder Point including isolating switch with indication lamp, cables, conduits, and all accessories | ea. | 1
5.1 | Supply, Install and Connect Oval bulkhead lamp with ring, eyelid or grid cover. Made of shockproof resin material, UV-rays stabilized, rust and corrosion-free. Suitable for wall and GX53 LED or E27, IP66 18w, LED Celling light , 2000 LM water proof light | ea. | 2
5.11 | Supply, Install and Connect LED Module, system flux 10,000 lm - 740 neutral white - Power supply unit - Beam category A1, projector, IP65 | ea. | 4
5.12 | Supply, Install and Connect LED 1200mm, 35W, Rated lumens 4200, CCT (K) 6500K, 120 lm/W, Rated lifetime, 30000 hrs @L70 25℃ | ea | 7
5.13 | Supplying, installing and testing Earthing System for the site includes galvanized steel strip 30x3 mm, welded each meter to its base steel structure, 3 sets of 19mm,Dia, 1.5m L,CU rods including 95 CU wire, pits with heavy duty cast iron covers, 10mm2 or 6mm2 insulated earthing of all metal parts that includes cable trays, water pipes, cable ladder, ac units, distribution boards bodies,PEC 40x4x0.4 mm2 in metal box, Earthing and grounding resistance must be =<2 ohm | Ls | 1
Total
Total Carried to Summary
Unit Legend:
| lm | linear meter
| sq m | square meter
| cu m | cubic meter
| ls | lump sum
| ea | each

## summary
Summary Sheet
Bill No. | Description | Total Price US $
1 | Mechanical Works
2 | Electrical Works
Total
Grand Total Including VAT
Percentage % discount or addition
Net Grand Total Including VAT
The sum of ………………………………………………. Including VAT US$
Contractor: ------------------------------------------------------------
Signature: ------------------------------------------------------------
Date: ------------------------------------------------------------